| INPUTS | Power Supply | Actual meaning |
| --- | --- | --- |
| D+ |  | Modbus Sensor Connection. (If Applicable) |
| D- |  |  |
| I0 | -V | -V for Stand by compressor (If Applicable) |
| I1 | -V | BOILER_HEATER1_FEEDBACK |
| I2 | -V | BOILER_HEATER2_FEEDBACK |
| I3 | -V | DRY_HEATER_FEEDBACK |
| I4 | +24 DVC | MAINS ON FEEDBACK |
| I5 | +24 DVC | COMPRESSOR1_FEEDBACK |
| I6 | +24 DVC | COMPRESSOR2_FEEDBACK |
| I7 | +24 DVC | WATER_LOW_LEVEL1 |
| I8 | +24 DVC | WATER_LOW_LEVEL2 |
| I9 | +24 DVC | DOOR_SENSOR |
| I10 | +24 DVC | Magnetic DOOR_UNLOCK (Only in Walk in Chambers) |
| I15 | +24 DVC | Lux Light Feedback (If Applicable) |
| I16 | +24 DVC | UV Light Feedback (If Applicable) |
| I23 |  | PLC Reset.(If Required.) |
| Outputs |  | Actual meaning |
| Q0 | -V | Hooter |
| Q1 | -V | Boiler Heater Selection. |
| Q2 | -V | DH SSR |
| Q3 | -V | BH SSR |
| Q4 | -V | Remote alarm |
| Q5 | -V | Door heater |
| Q6 | -V | spare |
| Q7 | -V | Door lock magnetic |
| Q8 | -V | DH safety |
| Q9 | -V | BH safety |
| Q10 | -V | CO1 |
| Q11 | -V | CO2 |
| Q12 | -V | Lux Light (If Applicable) |
| Q13 | -V | UV light (If Applicable) |

*Note: - D+ and D- is only for Modbus sensors (Scanner Sensor) communication.

*Note: - Q12 and Q13 Use for DF-H1 and DF-H2 (Defrost 1 and Defrost 2) in Thaw/ Deep Freezer      Chamber.